## PUBLIC_CIP & Non-CIP_Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation (For purposes of this document, each violation at issue is described as a “violation,” regardless of its procedural posture and whether it was a possible, or confirmed violation.) | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits" "Neither Admits nor Denies" "Agrees and Stipulates to the Facts" or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
RFC | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000692 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that its security monitoring process failed to detect and alert for unauthorized access attempts for two firewalls located on an electronic security perimeter (ESP). Specifically, RFC_URE1’s security management software tool was configured to alert RFC_URE1 to unauthorized access attempts based upon a threshold frequency of access denials from a specific IP address. RFC_URE1 did not configure two firewalls to report access denial events to the security management software tool. As a result, RFC_URE1’s security logging and alerts would not have functioned correctly if there had been unauthorized access attempts to the firewalls. | CIP-005-1 | R3/ R3.2 | Medium | Severe | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because RFC_URE1 configured the firewalls on the ESP to deny access by default, and therefore the Critical Cyber Assets (CCAs) within the ESP remained protected from unauthorized access attempts throughout the duration of the violation. Additionally, the security management software tool did log all permitted access attempts and firewall configuration changes. | The date on which RFC_URE1 was subject to compliance with CIP-005-1. | The date on which RFC_URE1 corrected the configuration of the firewalls to log and report access denial events to the security management tool. | $30,000 (for RFC201000692, RFC201000693, RFC201000694, RFC201100752, RFC201100753, and RFC201100754) | Self-Report | RFC_URE1 corrected the configuration of its firewalls to log and alert RFC_URE1 to all denied unauthorized access attempts. | 2010-10-12 | 2011-08-17 | Neither Admits nor Denies | RFC_URE1 had a compliance program at the time of the violation which ReliabilityFirst considered a mitigating factor.
RFC | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000693 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it discovered a network switch that had ports and services that were not required for normal or emergency operations but that were still enabled, in violation of CIP-007-1 R2. While performing an annual vulnerability assessment, RFC_URE1 discovered that the network switch, which is located inside the electronic security perimeter (ESP), had ports and services that were not required for normal and emergency operations, but that were still enabled | CIP-007-1 | R2/ R2.1, R2.2 | Medium | Severe | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the network switch is located behind the ESP firewall and is therefore not accessible from outside the ESP. | The date on which RFC_URE1 was subject to compliance with CIP-007-1. | The date on which RFC_URE1 disabled the ports and services that were enabled on the network switch. | $30,000 (for RFC201000692, RFC201000693, RFC201000694, RFC201100752, RFC201100753, and RFC201100754) | Self-Report | RFC_URE1 disabled the ports and services that were enabled on the network switch. | 2010-11-19 | 2011-08-16 | Neither Admits nor Denies | RFC_URE1 had a compliance program at the time of the violation which ReliabilityFirst considered a mitigating factor.
RFC | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000694 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it failed to remove or disable factory default accounts on a network switch (the same network switch as RFC201000693), and failed to meet password requirements as required by CIP-007-1 R5. Specifically, RFC_URE1 discovered a network switch within the electronic security perimeter (ESP) had two factory default accounts that RFC_URE1 had not removed, disabled, or renamed. Additionally, RFC_URE1 failed to create passwords for the two factory default accounts that conform with the requirements of CIP-007-1 R5.3, prior to placing them into service. RFC_URE1 discovered this oversight during its annual vulnerability assessment. | CIP-007-1 | R5 | Lower | Severe | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the network switch containing the two factory default accounts is located behind the ESP firewall and is therefore not accessible from outside the ESP. | The date on which RFC_URE1 was subject to compliance with CIP-007-1. | The date on which RFC_URE1 set complex passwords for the two factory default accounts on the network switch. | $30,000 (for RFC201000692, RFC201000693, RFC201000694, RFC201100752, RFC201100753, and RFC201100754) | Self-Report | RFC_URE1 set complex passwords for the two factory default accounts on the network switch that conform to CIP-007-1 R5.3. | 2010-11-19 | 2011-08-16 | Neither Admits nor Denies | RFC_URE1 had a compliance program at the time of the violation which ReliabilityFirst considered a mitigating factor.
RFC | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100752 | Settlement Agreement | ReliabilityFirst conducted a compliance audit of RFC_URE1 (the Compliance Audit). During the Compliance Audit, ReliabilityFirst discovered that RFC_URE1’s physical security plan failed to satisfy two requirements of CIP-006-1. First, RFC_URE1’s physical security plan failed to address response to loss and prohibition of inappropriate use of physical access controls, as required by CIP-006-1 R1.4. Second, RFC_URE1’s physical security plan stated that it would be updated within 90 calendar days of a physical security system design or configuration change. Although Version 1 of CIP-006, R1.7 allowed for a 90-day period to update a physical security plan, on April 1, 2010 Version 2 of CIP-006 took effect, which requires a narrower, 30-day update period. Therefore, from the effective date of CIP-006-2, RFC_URE1 failed to include a requirement in its physical security plan to update the physical security plan within 30 days of a physical security system design or configuration change. | CIP-006-1 | R1/ R1.4, R1.7 | Medium | Severe | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because although RFC_URE1’s physical security plan did not include information about responding to loss or a prohibition of inappropriate use of physical access controls, RFC_URE1 addressed these topics in another RFC_URE1 document, and trained its employees on these topics. Additionally, although RFC_URE1’s physical security plan stated that RFC_URE1 must update the physical security plan within 90 days of any changes rather than within 30 days, RFC_URE1 made no changes to its physical security plan during the duration of this violation, and did not need to make any updates. | The date on which RFC_URE1 was required to be compliant with CIP-006-1. | The date on which RFC_URE1 revised its physical security plan to comply with CIP-006-1 R1.4 and R1.7. | $30,000 (for RFC201000692, RFC201000693, RFC201000694, RFC201100752, RFC201100753, and RFC201100754) | Compliance Audit | RFC_URE1 revised its physical security plan to address response to loss and prohibition of inappropriate use of physical access controls, and to include a requirement to update the physical security plan within 30 days of a physical security system design or configuration change. | 2011-01-27 | 2011-08-19 | Neither Admits nor Denies | RFC_URE1 had a compliance program at the time of the violation which ReliabilityFirst considered a mitigating factor.
RFC | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100753 | Settlement Agreement | ReliabilityFirst conducted a compliance audit of RFC_URE1 (the Compliance Audit). During the Compliance Audit, ReliabilityFirst discovered that RFC_URE1’s Cyber Security incident response plan failed to include a process for updating the Cyber Security incident response plan within 30 calendar days of any changes. Instead, RFC_URE1’s Cyber Security incident response plan included a process for updating the Cyber Security incident response plan within 90 calendar days of any changes. Although Version 1 of CIP-008 allowed for a 90-day period to update the Cyber Security incident response plan, on April 1, 2010 Version 2 of CIP-008 took effect, which requires a narrower, 30-day period. Therefore, from the effective date of CIP-008-2, RFC_URE1 failed to comply with CIP-008-2 R1.4. | CIP-008-2 | R1 | Lower | High | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because although RFC_URE1’s Cyber Security incident response plan stated that RFC_URE1 must update the Cyber Security incident response plan within 90 days of any changes rather than within 30 days, RFC_URE1 made no changes to the Cyber Security incident response plan during the time period of this violation, and therefore, did not need to make any updates. | The date on which RFC_URE1's Cyber Security incident response plan was not compliant with the updated Version 2 of CIP-008. | The date on which RFC_URE1 revised its Cyber Security incident response plan to include a process for updating the Cyber Security incident response plan within 30 calendar days of changes. | $30,000 (for RFC201000692, RFC201000693, RFC201000694, RFC201100752, RFC201100753, and RFC201100754) | Compliance Audit | RFC_URE1 revised its Cyber Security incident response plan to include a process for updating the Cyber Security incident response plan within 30 calendar days of any changes. | 2011-01-27 | 2011-08-12 | Neither Admits nor Denies | RFC_URE1 had a compliance program at the time of the violation which ReliabilityFirst considered a mitigating factor.
RFC | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100754 | Settlement Agreement | ReliabilityFirst conducted a compliance audit of RFC_URE1 (the Compliance Audit). During the Compliance Audit, ReliabilityFirst discovered that RFC_URE1’s recovery plan failed to satisfy both sub-requirements of CIP-009-1 R1. First, RFC_URE1’s recovery plan failed to specify events or conditions of varying duration and severity that would activate the recovery plan, as required by R1.1. Second, RFC_URE1’s recovery plan failed to define the roles and responsibilities of responders, as required by R1.2. In addition, RFC_URE1 failed to address all of its Critical Cyber Assets (CCAs) in its recovery plan. The plan addressed only six of RFC_URE1’s 13 total CCAs. | CIP-009-1 | R1 | Medium | Severe | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because although RFC_URE1 did not specify events or conditions of varying duration and severity that would activate the recovery plan, it did address responding to events of varying duration and severity in its CIP-008 Cyber Security Incident response plan. Similarly, although RFC_URE1 did not define the roles and responsibilities of responders in its recovery plan, it did address those roles and responsibilities in its CIP-003 cyber security policy. RFC_URE1 represents that the information that it failed to specifically state within its recovery plan would have been readily available to authorized RFC_URE1 personnel responding to an event requiring the recovery of CCAs. | The date on which RFC_URE1 was required to be compliant with CIP-009-1. | The date on which RFC_URE1 revised its recovery plan to comply with CIP-009-1 R1. | $30,000 (for RFC201000692, RFC201000693, RFC201000694, RFC201100752, RFC201100753, and RFC201100754) | Compliance Audit | RFC_URE1 revised its recovery plan to specify events or conditions of varying duration and severity that would activate the recovery plan, define the roles and responsibilities of responders, and address all of RFC_URE1’s CCAs. | 2011-01-27 | 2011-08-16 | Neither Admits nor Denies | RFC_URE1 had a compliance program at the time of the violation which ReliabilityFirst considered a mitigating factor.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201000689 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst concerning a violation of CIP-004-2 R4.1, due to RFC_URE2’s failure to update the list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets within seven days of a change of personnel with such access to Critical Cyber Assets. Specifically, RFC_URE2 terminated an employee for cause but did not update the list of personnel with access to Critical Cyber Assets within seven days of the change in access rights. Nevertheless, RFC_URE2 did revoke the terminated employee’s access within 24 hours, as required by CIP-004-2 R4.2. RFC_URE2 violated CIP-004-2 R4.1 by failing to update the list of personnel who have access to Critical Cyber Assets within seven days of any change of personnel with such access to Critical Cyber Assets. | CIP-004-2 | R4 (R4.1) | Lower | High | ReliabilityFirst determined the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because RFC_URE2 revoked access control cards, passwords, and appropriate accounts from the terminated employee within twenty-four hours of the employee’s termination. In addition, while the terminated employee was on the list of personnel who have access to Critical Cyber Assets because of his access to electronic confidential records, the employee did not have electronic access or control privileges to the Supervisory Control and Data Acquisition (SCADA) system or any other Critical Cyber Assets. | The date by which RFC_URE2 was required to update its Critical Cyber Assets access list. | The date on which RFC_URE2 updated its list of personnel with access to Critical Cyber Assets to remove the terminated individual. | $1,000 (Settlement for RFC201000689) | Self-Report | RFC_URE2 updated its list of personnel with access to Critical Cyber Assets to reflect the updated accesses to Critical Cyber Assets. In addition, RFC_URE2 informed all managers of the need to report the change in status of any employee on the CIP confidential list. | 2011-01-04 | 2011-05-24 | Agrees and Stipulates to the Facts | ReliabilityFirst determined that there was nothing in the record to suggest that broader corporate issues were implicated.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201000457 | Settlement Agreement | RFC_URE3 submitted a Self-Report to ReliabilityFirst concerning a violation of CIP-005-1 R3.2. RFC_URE3’s internal computer network supports RFC_URE3’s Energy Management Systems (EMS). RFC_URE3’s interior firewalls separate the internal computer network from its general business network. The interior firewalls serve as the Electronic Security Perimeter (ESP) for RFC_URE3’s internal computer network, as well as the access points to the ESP. While conducting an internal review , RFC_URE3 discovered that it had not fully enabled its logging and alerting system to alert for unauthorized access attempts to the ESP, as required by CIP-005-1 R3.2. ReliabilityFirst determined RFC_URE3 failed to implement its processes for monitoring and logging access at access points to the ESP. Specifically, RFC_URE3 failed to enable its logging and alert system for attempts at or actual unauthorized access to RFC_URE3's ESP, as required by CIP-005-1 R3.2. | CIP-005-1 | R3 (R3.2) | Medium | Severe | ReliabilityFirst determined this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because, for the duration of the violation, RFC_URE3’s internal computer network was monitored by two intrusion detection software products. Although RFC_URE3’s intrusion detection software did not monitor ESP access points, in the event of actual unauthorized access to or suspicious behavior on RFC_URE3’s ESP, the intrusion detection software would detect the intrusion or suspicious behavior and notify RFC_URE3. In addition, RFC_URE3 reviewed logs from January 1, 2010, through August 12, 2010, the date RFC_URE3 reconfigured its ESP settings to comply with CIP-005-1, R3.2, and found that there were no attempts to access the ESP from any unauthorized IP addresses. | The date RFC_URE3 failed to implement its processes for monitoring and logging access points to the ESP. | The date RFC_URE3 fully enabled detection and alerting for unauthorized access attempts on its ESP. | $6,000 (Settlement of RFC201000457) | Self-Report | RFC_URE3 reconfigured its ESP to send system logging alerts to the administrator and supervisor of the EMS . In addition, RFC_URE3 conducted a test to ensure all configured controls were working as required, which was successful. Finally, RFC_URE3 now retains all logs for a rolling 365-day cycle and all alerts for a minimum of 90 days. | 2010-08-12 | 2011-05-13 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE3’s compliance program as mitigating factors.
RFC | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC201000395 | Settlement Agreement | During a Spot Check of RFC_URE4, ReliabilityFirst determined that RFC_URE4 failed to identify six of its Cyber Assets that either use a routable protocol to communicate outside the Electronic Security Perimeter or use a routable protocol within a control center as Critical Cyber Assets. First, RFC_URE4 failed to identify four remote workstations that communicate outside the Electronic Security Perimeter using a routable protocol as Critical Cyber Assets, in violation of CIP-002-1 R3.1. These four remote workstations are enabled to monitor and control the bulk power system (BPS). Second, RFC_URE4 also failed to identify two of its workstations, which use a routable protocol within a control center as Critical Cyber Assets, in violation of CIP-002-1 R3.2. (RFC_URE4 did, however, list the two workstations as Cyber Assets.) | CIP-002-1 | R3 | High | Severe | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the BPS. All users of the six workstations at issue had completed personnel risk assessments and had authorized access to Critical Cyber Assets. The four workstations that used a routable protocol to communicate outside the Electronic Security Perimeter utilized three levels of password protection, which provided protection against unauthorized users from utilizing the workstations to control any BPS assets. The two workstations that used a routable protocol within a control center remained within the Physical Security Perimeter and the Electronic Security Perimeter, and therefore received all the same protections as Critical Cyber Assets. | The date on which RFC_URE4 was subject to compliance with CIP-002-1 R3. | The date on which RFC_URE4 reconfigured its workstations. | $16,500 (for RFC201000395, RFC201000398, and RFC201000399) | Spot Check | On August 31, 2010, RFC_URE4 submitted to ReliabilityFirst its mitigation plan to address the violation of CIP-002-1 R3. In this mitigation plan, RFC_URE4 memorialized the actions it took to address the violation of CIP-002-1 R3. RFC_URE4 reconfigured the four workstations that communicated outside the Electronic Security Perimeter, and removed their control functionality. These four workstations are currently not classified as Critical Cyber Assets, since they are now limited to monitoring functions and are therefore not "essential to the operation of the Critical Asset." RFC_URE4 also added the two workstations that use a routable protocol within the control center to the RFC_URE4 Critical Cyber Asset list. | 2010-06-23 | 2010-10-22 | Admits | ReliabilityFirst considered RFC_URE4's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
RFC | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC201000398 | Settlement Agreement | During a Spot Check, ReliabilityFirst determined that RFC_URE4 failed to ensure that a significant change to existing Cyber Assets within the Electronic Security Perimeter did not adversely affect existing security controls. Specifically, ReliabilityFirst examined evidence of a software upgrade, including RFC_URE4's testing of the software upgrade, but the evidence of testing did not provide sufficient information to establish that the software upgrade did not adversely affect RFC_URE4's cyber security controls. RFC_URE4 provided evidence of later testing of the software upgrade, which showed significant discrepancies from the evidence of the original testing. | CIP-007-1 | R1 | Medium | High | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE4 utilizes two fully redundant systems at its primary location and two fully redundant systems at its backup location. These systems are upgraded at different times, thereby providing protection in the event of adverse effects from the software upgrade. | The date on which RFC_URE4 implemented a change to existing Cyber Assets within the ESP without ensuring that the change did not adversely affect existing security controls. | The date on which RFC_URE4 documented testing of cyber security controls. | $16,500 (for RFC201000395, RFC201000398, and RFC201000399) | Spot Check | On August 31, 2010, RFC_URE4 submitted to ReliabilityFirst its mitigation plan to address the violation of CIP-007-1 R1. In this mitigation plan, RFC_URE4 memorialized the actions it took to address the violation of CIP-007-1 R1. RFC_URE4 created a check list for documenting all future testing of changes to Cyber Assets to ensure that it properly tests security controls both before and after the changes to Cyber Asset are made. | 2010-06-22 | 2010-10-22 | Admits | ReliabilityFirst considered RFC_URE4's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
RFC | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC201000399 | Settlement Agreement | During a Spot Check, ReliabilityFirst determined that RFC_URE4 failed to demonstrate that it annually tested its Cyber Security Incident response plan. Therefore, RFC_URE4 failed to ensure that its Cyber Security Incident response plan is tested at least annually. ReliabilityFirst found that RFC_URE4 violated CIP-008-1 R1.6 by failing to ensure that its Cyber Security Incident response plan is tested at least annually. | CIP-008-1 | R1.6 | Lower | High | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although, RFC_URE4 did not produce sufficient documentation at the Spot Check to establish compliance with CIP-008-1 R1, RFC_URE4 represents that it tested the Cyber Security Incident response plan. Furthermore, RFC_URE4 has conducted a recent test of the Cyber Security Incident response plan, which demonstrates the efficacy of the Cyber Security Incident response plan in responding to incidents. | The date on which RFC_URE4 was subject to compliance with CIP-008-1 R1. | The date on which RFC_URE4 developed a test report form for its Cyber Security Incident response plan. | $16,500 (for RFC201000395, RFC201000398, and RFC201000399) | Spot Check | On August 31, 2010, RFC_URE4 submitted to ReliabilityFirst its mitigation plan to address the violation of CIP-008-1 R1.6. RFC_URE4 memorialized the actions it took to address the violation of CIP-008-1 R1.6. RFC_URE4 developed a test report form to cover all steps required in RFC_URE4's Cyber Security Incident response plan. | 2010-06-21 | 2010-10-22 | Admits | ReliabilityFirst considered RFC_URE4's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
ReliabilityFirst | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201000393 | Settlement Agreement | RFC_URE5 submitted a Self-Report indicating a violation of CIP-004-1 R4.2, to ReliabilityFirst. RFC_URE5 failed to remove one employee (Employee A) which no longer required access to CCAs from their Critical Cyber Asset (CCA) Electronic Access List within seven days. On March 22, 2010, RFC_URE5 designated Employee A as inactive but did not remove CCA electronic access or update the CCA Electronic Access List until May 11, 2010. RFC_URE5 submitted a Self-Report update indicating that the violation of CIP-004-1 R4.2 expanded in scope. RFC_URE5 did not remove an additional employee (Employee B) from its CCA Physical Access list within seven days of Employee B no longer requiring access. Specifically, Employee B resigned from the company effective August 7, 2010, but was not removed from the Physical Access List until August 18, 2010. RFC_URE5 did revoke all access rights for Employee B on August 7, 2010. RFC_URE5 submitted a second update to the Self-Report. RFC_URE5 granted an employee (Employee C) temporary access to a Physical Security Perimeter (PSP) from June 2, 2010 to June 4, 2010, but failed to remove Employee C from the CCA Physical Access List within seven calendar days of revoking Employee C's access on June 4, 2010. RFC_URE5 did not remove Employee C from the CCA Physical Access List until September 21, 2010. RFC_URE5 violated CIP-004-1 R4 on three separate occasions when it failed to remove Employees A, B and C from its CCA Access Lists within seven days of those employees no longer requiring access to CCAs. | CIP-004-1 | R4/ R4.2 | Medium | Moderate | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because Employee A did not have physical access to the PSP in which the CCAs reside during the time period of the violation. Moreover the CCAs could not be electronically accessed by Employee A from anywhere outside the PSP. Employee B did not have physical access to the PSP during the time period of the violation. RFC_URE5 collected all access devices that would allow Employee B to physically enter the PSP on the same day as Employee B resigned. As a result, it was impossible for Employee B to physically access the PSP after August 7, 2010. Employee B also had completed CIP training and had a clear personnel risk assessment (PRA) in place at the time of the violation. Although Employee C did have key card access to the PSP, Employee C did not have key access to the perimeter gate surrounding the PSP, and did not have a non-forcible means of access to the perimeter gate surrounding the PSP. Additionally, Employee C had completed CIP training and had a clear PRA in place at the time of the violation. | The date by which RFC_URE5 should have removed Employee A from the CCA Electronic Access List. | The date RFC_URE5 removed Employee C from the CCA Physical Access List. | $30,000 (for RFC201000393, RFC201000394, and RFC201000773) | Self-Report | RFC_URE5 updated the CCA Access Lists to reflect the personnel status changes for Employees A, B, and C. RFC_URE5 also removed Employee C's key access to the PSP. RFC_URE5 reviewed the incidents of non-compliance and the procedures that were not followed, and then revised those procedures. Senior management from the Human Resources and Legal departments reinforced the importance of adhering to the CIP procedures to the entire company. RFC_URE5 developed a process to compare its Human Resources personnel database with the database used to identify roles in the CIP Compliance program. RFC_URE5 now generates a daily report to identify any changes in the status of an employee with physical or electronic access to the PSP. | 2011-02-22 | 2011-06-07 | Neither Admits nor Denies | The parent company of RFC_URE5 had a compliance program at the time of the violation which ReliabilityFirst considered a mitigating factor. RFC_URE5 does not have any prior violations of the CIP Reliability Standards. ReliabilityFirst did consider the repetitive nature of the violations addressed within this Settlement Agreement as an aggravating factor in the penalty determination. In considering the instant violations, ReliabilityFirst did not observe any evidence of involvement of the entire holding company system or other affiliates.
ReliabilityFirst | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201000394 | Settlement Agreement | RFC_URE5 submitted a Self-Report indicating a violation of CIP-006-1 R2 to ReliabilityFirst. On March 31, 2010, a RFC_URE5 employee with authorized unescorted physical access to a Physical Security Perimeter (PSP) (Authorized Employee) failed to manage a PSP access point on three occasions, for a combined duration of approximately 15 minutes. Individuals without authorized access were performing maintenance on the floor below the PSP access point, and as a result of the maintenance, RFC_URE5 left the door that is used to secure the PSP ajar. During the time period that the door to the PSP was ajar, the Authorized Employee left the area on three occasions and failed to monitor this PSP access point. RFC_URE5 violated CIP-006-1 R2 by failing to implement its physical security plan and manage physical access to all access points to the PSP. | CIP-006-1 | R2 | Medium | High | ReliabilityFirst determined this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system to the reliability of the bulk power system because RFC_URE5 had a documented Physical Security Plan in place that addressed the requirement to control access points to the PSP, and trained the Authorized Employee on this requirement. The PSP access point is located within an access-controlled facility and also within a further restricted, access-controlled, corporate data center. Therefore, the PSP access point has multiple layers of protection. The PSP is also under video surveillance, which allowed RFC_URE5 to monitor any attempts by an unauthorized individual to enter through this PSP access point. No such attempts were made during the alleged violation. Finally, the violation was short in duration, lasting approximately 15 minutes. | The time period which RFC_URE5 failed to manage physical access to a PSP for 15 minutes. | When RFC_URE5 returned to monitoring physical access to the PSP. | $30,000 (for RFC201000393, RFC201000394, and RFC201000773) | Self-Report | RFC_URE5 enhanced its Physical Security Plan, and developed a targeted CIP training session specifically for business services employees who may be involved in maintenance activities at PSP access points. The CIP training session reinforced the companies' visitor escort policy and clarified the requirements for monitoring PSP access points. RFC_URE5 conducted additional CIP training sessions for RFC_URE5 employees and contractors. RFC_URE5 also posted signs at PSP access points and distributed laminated cards to remind employees and contractors that access is restricted to authorized individuals, and detail requirements for access control, visitor escorting, and entry logging. | 2010-08-30 | 2011-04-13 | Neither Admits nor Denies | The parent company of RFC_URE5 had a compliance program at the time of the violation which ReliabilityFirst considered a mitigating factor. RFC_URE5 does not have any prior violations of the CIP Reliability Standards. ReliabilityFirst did consider the repetitive nature of the violations addressed within this Settlement Agreement as an aggravating factor in the penalty determination. In considering the instant violations, ReliabilityFirst did not observe any evidence of involvement of the entire holding company system or other affiliates.
ReliabilityFirst | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201000773 | Settlement Agreement | RFC_URE5 submitted a Self-Report indicating a violation of CIP-004-1 R3 to ReliabilityFirst. On October 1, 2010, RFC_URE5 discovered that it provided an employee (Employee 1) with authorized unescorted physical access to a Physical Security Perimeter (PSP) on January 1, 2010, who did not have a personnel risk assessment (PRA) within 30 days of access. On October 1, 2010, RFC_URE5 also discovered that it provided a second employee (Employee 2) with authorized unescorted physical access to a PSP on April 15, 2010, who did not have a PRA within 30 days of access. Finally, on October 14, 2010, RFC_URE5 discovered that it provided a third employee (Employee 3) with authorized unescorted physical access to a PSP on October 13, 2010, who did not have a PRA within 30 days of access. RFC_URE5 violated CIP-004-1 R3 by failing to conduct PRAs for three employees within 30 days of providing those employees with authorized access to a PSP. | CIP-004-1 | R3 | Medium | High | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because Employee 1 and Employee 2 did not enter the PSP during the time period of the violation. Additionally, RFC_URE5 later conducted PRAs for Employee 1,2, and 3, which identified no issues. Employee 3 did not have key access or any other means of non-forcible access to the perimeter gate surrounding the PSP at issue, and RFC_URE5's records of Employee 3 indicate that Employee 3 never attempted to access the PSP during the violation. | 30 days after Employee 1 had access to the PSP without a PRA. | The date on which RFC_URE5 revoked the authorized unescorted physical access rights for Employee 3. | $30,000 (for RFC201000393, RFC201000394, and RFC201000773) | Self-Report | RFC_URE5 revoked access rights to Employees 1, 2, and 3. RFC_URE5 also conducted PRAs for Employees 1, 2 and 3, which identified no issues. Additionally, RFC_URE5 is adding a control to its PSP access request process which will require the requestor to confirm PRA status before submitting a request for access to the PSP. | 2011-02-22 | 2011-06-07 | Neither Admits nor Denies | The parent company of RFC_URE5 had a compliance program at the time of the violation which ReliabilityFirst considered a mitigating factor. RFC_URE5 does not have any prior violations of the CIP Reliability Standards. ReliabilityFirst did consider the repetitive nature of the violations addressed within this Settlement Agreement as an aggravating factor in the penalty determination. In considering the instant violations, ReliabilityFirst did not observe any evidence of involvement of the entire holding company system or other affiliates.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001887 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence, WECC determined that WECC_URE1 failed to demonstrate that it had procedures in place for the recognition of sabotage events and for making its operating personnel aware of sabotage events on its facilities and on multi-site sabotage events affecting larger portions of the Interconnection, in violation of CIP-001-1 R1. | CIP-001-1 | R1 | Medium | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity but has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. WECC determined that although sabotage recognition procedures helps personnel assess the sabotage event and determine further actions, the impact on the BPS from a potential sabotage event at WECC_URE1 would have been very limited because of WECC_URE1's limited size, single interconnection to another entity, and unique supply profile serving that other entity only. | The date on which WECC_URE1 was subject to compliance with CIP-001-1 R1. | The date on which WECC_URE1 documented and implemented its sabotage reporting procedure. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan, covering the violations of CIP-001-1 R1-R4. According to the Mitigation Plan, WECC_URE1 implemented procedures for the recognition of sabotage events and for making its personnel aware of such events on its facilities and of multi-site sabotage affecting larger portions of the Interconnection. WECC_URE1 also implemented procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection, provided its operating personnel with sabotage response guidelines, established contacts with local FBI officials and developed appropriate reporting procedures. WECC_URE1 submitted its sabotage recognition and reporting procedure to WECC as evidence of its Mitigation Plan completion. | 2010-08-20 | 2011-02-08 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001888 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. As a result, WECC determined that WECC_URE1 failed to demonstrate that it had procedures in place for the communication of information concerning sabotage events to appropriate parties in the Interconnection. | CIP-001-1 | R2 | Medium | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. WECC determined that although notifying other operating systems of possible sabotage events increases the situational awareness of the entities interconnected to the BPS, the impact on the BPS from a potential failure to communicate a sabotage event at WECC_URE1 would have been very limited because of WECC_URE1's limited size and single interconnection to another entity, which minimizes the risk to the BPS. | The date on which WECC_URE1 was subject to compliance with CIP-001-1 R2. | The date on which WECC_URE1 documented and implemented its sabotage reporting procedure. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan, covering the violations of CIP-001-1 R1-R4. According to the Mitigation Plan, WECC_URE1 implemented procedures for the recognition of sabotage events and for making its personnel aware of such events on its facilities and of multi-site sabotage affecting larger portions of the Interconnection. WECC_URE1 also implemented procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection, provided its operating personnel with sabotage response guidelines, established contacts with local FBI officials and developed appropriate reporting procedures. WECC_URE1 submitted its sabotage recognition and reporting procedure to WECC as evidence of its Mitigation Plan completion. | 2010-08-20 | 2011-02-08 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001889 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. As a result, WECC determined that WECC_URE1 failed to provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. | CIP-001-1 | R3 | Medium | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. WECC determined that although a lack of sabotage communication guidelines could delay corrective actions on behalf of the entity, the impact on the BPS from a potential failure of WECC_URE1's personnel to report a sabotage event would have been very limited because of WECC_URE1's limited size and single interconnection to another entity, which minimizes the risk to the BPS. | The date on which WECC_URE1 was subject to compliance with CIP-001-1 R3. | The date on which WECC_URE1 documented and implemented its sabotage reporting procedure. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan, covering the violations of CIP-001-1 R1-R4. According to the Mitigation Plan, WECC_URE1 implemented procedures for the recognition of sabotage events and for making its personnel aware of such events on its facilities and of multi-site sabotage affecting larger portions of the Interconnection. WECC_URE1 also implemented procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection, provided its operating personnel with sabotage response guidelines, established contacts with local FBI officials and developed appropriate reporting procedures. WECC_URE1 submitted its sabotage recognition and reporting procedure to WECC as evidence of its Mitigation Plan completion. | 2010-08-20 | 2011-02-08 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001890 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. As a result, WECC determined that WECC_URE1 failed to establish communications contacts with local FBI officials and to develop reporting procedures. | CIP-001-1 | R4 | Medium | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. WECC determined that although a lack of reporting procedures to the local FBI could lead to sabotage events being unreported, the impact on the BPS from a potential failure of WECC_URE1's personnel to contact the FBI would have been very limited because of WECC_URE1's limited size and single interconnection to another entity, which minimizes the risk to the BPS. | The date on which WECC_URE1 was subject to compliance with CIP-001-1 R4. | The date on which WECC_URE1 documented and implemented its sabotage reporting procedure. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan, covering the violations of CIP-001-1 R1-R4. According to the Mitigation Plan, WECC_URE1 implemented procedures for the recognition of sabotage events and for making its personnel aware of such events on its facilities and of multi-site sabotage affecting larger portions of the Interconnection. WECC_URE1 also implemented procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection, provided its operating personnel with sabotage response guidelines, established contacts with local FBI officials and developed appropriate reporting procedures. WECC_URE1 submitted its sabotage recognition and reporting procedure to WECC as evidence of its Mitigation Plan completion. | 2010-08-20 | 2011-02-08 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002056 | Settlement Agreement | WECC notified WECC_URE1 that WECC was initiating a semi-annual CIP Self-Certification process. WECC_URE1 filed a Self-Certification statement and reported that its compliance status for CIP-002-1 R1-R4 was "Not Started." WECC reviewed WECC_URE1's Self-Certification and determined that WECC_URE1 failed to identify and document a risk-based assessment methodology (RBAM) to use to identify its Critical Assets. | CIP-002-1 | R1 | Medium | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because after WECC_URE1 provided and implemented its RBAM following WECC's audit, it became apparent that WECC_URE1 did not have any Critical Assets or Critical Cyber Assets on its system and, therefore, WECC concluded that there had been no actual risk to the BPS. Also, WECC_URE1's size minimizes the risk to the BPS. WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. | The date on which WECC_URE1 was subject to compliance with CIP-002-1 R1. | The date on which WECC_URE1 documented and implemented its methodology document. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Self-Certification | WECC_URE1 submitted a Mitigation Plan covering the violations of CIP-002-1 R1-R4. According to the Mitigation Plan, WECC_URE1 developed and implemented a formal Critical Asset Identification Methodology to be applied in identifying Critical Assets and Critical Cyber Assets. WECC_URE1 also will annually update its list of Critical Assets and Critical Cyber Assets. The methodology document submitted as evidence of compliance included documentation of WECC_URE1's application of its methodology for the purpose of assessing whether WECC_URE1 owns, operates, or controls Critical Assets and Critical Cyber Assets as well as the corresponding asset lists and designated senior manager approvals. | 2010-11-15 | 2011-02-02 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002057 | Settlement Agreement | WECC notified WECC_URE1 that WECC was initiating a semi-annual CIP Self-Certification process. WECC_URE1 filed a Self-Certification statement and reported that its compliance status for CIP-002-1 R1-R4 was "Not Started." WECC reviewed WECC_URE1's Self-Certification submittal and determined that WECC_URE1failed to develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology (RBAM) required in R1. | CIP-002-1 | R2 | High | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because after WECC_URE1 provided and implemented its RBAM following WECC's audit, it became apparent that WECC_URE1 did not have any Critical Assets or Critical Cyber Assets on its system and, therefore, WECC concluded that there had been no actual risk to the BPS. Also, WECC_URE1's size minimizes the risk to the BPS. WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. | The date on which WECC_URE1 was subject to compliance with CIP-002-1 R2. | The date on which WECC_URE1 documented and implemented its methodology document, including a list of Critical Assets. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Self-Certification | WECC_URE1 submitted a Mitigation Plan covering the violations of CIP-002-1 R1-R4. According to the Mitigation Plan, WECC_URE1 developed and implemented a formal Critical Asset Identification Methodology to be applied in identifying Critical Assets and Critical Cyber Assets. WECC_URE1 also will annually update its list of Critical Assets and Critical Cyber Assets. The methodology document submitted as evidence of compliance included documentation of WECC_URE1's application of its methodology for the purpose of assessing whether WECC_URE1 owns, operates, or controls Critical Assets and Critical Cyber Assets as well as the corresponding asset lists and designated senior manager approvals. | 2010-11-15 | 2011-02-02 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002058 | Settlement Agreement | WECC notified WECC_URE1 that WECC was initiating a semi-annual CIP Self-Certification process. WECC_URE1 filed a Self-Certification statement and reported that its compliance status for CIP-002-1 R1-R4 was "Not Started." WECC reviewed WECC_URE1's Self-Certification submittal and determined that WECC_URE1failed to develop a list of its associated Critical Cyber Assets that are essential to the operation of the Critical Assets. | CIP-002-1 | R3 | High | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because after WECC_URE1 provided and implemented its RBAM following WECC's audit, it became apparent that WECC_URE1 did not have any Critical Assets or Critical Cyber Assets on its system and, therefore, WECC concluded that there had been no actual risk to the BPS. Also, WECC_URE1's size minimizes the risk to the BPS. WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. | The date on which WECC_URE1 was subject to compliance with CIP-002-1 R3. | The date on which WECC_URE1 documented and implemented its methodology document, including a list of associated Critical Cyber Assets. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Self-Certification | WECC_URE1 submitted a Mitigation Plan covering the violations of CIP-002-1 R1-R4. According to the Mitigation Plan, WECC_URE1 developed and implemented a formal Critical Asset Identification Methodology to be applied in identifying Critical Assets and Critical Cyber Assets. WECC_URE1 also will annually update its list of Critical Assets and Critical Cyber Assets. The methodology document submitted as evidence of compliance included documentation of WECC_URE1's application of its methodology for the purpose of assessing whether WECC_URE1 owns, operates, or controls Critical Assets and Critical Cyber Assets as well as the corresponding asset lists and designated senior manager approvals. | 2010-11-15 | 2011-02-02 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002059 | Settlement Agreement | WECC notified WECC_URE1 that WECC was initiating a semi-annual CIP Self-Certification process. WECC_URE1 filed a Self-Certification statement and reported that its compliance status for CIP-002-1 R1-R4 was "Not Started." WECC reviewed WECC_URE1's Self-Certification submittal and determined that WECC_URE1failed to have a senior manager or delegate approve annually the list of WECC_URE1's Critical Assets or Critical Cyber Assets. | CIP-002-1 | R4 | Lower | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because after WECC_URE1 provided and implemented its RBAM following WECC's audit, it became apparent that WECC_URE1 did not have any Critical Assets or Critical Cyber Assets on its system and, therefore, WECC concluded that there had been no actual risk to the BPS. Also, WECC_URE1's size minimizes the risk to the BPS. WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. | The date on which WECC_URE1 was subject to compliance with CIP-002-1 R4. | The date on which WECC_URE1 documented and implemented its methodology document, including senior manager or delegate approval. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Self-Certification | WECC_URE1 submitted a Mitigation Plan covering the violations of CIP-002-1 R1-R4. According to the Mitigation Plan, WECC_URE1 developed and implemented a formal Critical Asset Identification Methodology to be applied in identifying Critical Assets and Critical Cyber Assets. WECC_URE1 also will annually update its list of Critical Assets and Critical Cyber Assets. The methodology document submitted as evidence of compliance included documentation of WECC_URE1's application of its methodology for the purpose of assessing whether WECC_URE1 owns, operates, or controls Critical Assets and Critical Cyber Assets as well as the corresponding asset lists and designated senior manager approvals. | 2010-11-15 | 2011-02-02 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001893 | Settlement Agreement | On December 4, 2009, WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence as requested by WECC, WECC determined that WECC_URE1 failed to provide evidence that it had documented its Facility Rating Methodology, as required by FAC-008-1 R1. | FAC-008-1 | R1 | Lower | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because of its limited size and a single interconnection to the BPS. WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. | The date on which WECC_URE1 was subject to compliance with FAC-008-1 R1. | The date on which WECC_URE1 documented its Facility Ratings Methodology. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan for FAC-008-1 R1. According to the Mitigation Plan, WECC_URE1 documented a Facility Rating Methodology for facilities and equipment at the WECC_URE1 generating facility, including the generator, transmission conductors, transformers, relay protective devices and terminal equipment. As evidence of compliance, WECC_URE1 submitted its Facility Rating Methodology. | 2010-09-08 | 2011-04-05 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001896 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence as requested by WECC on several occasions, WECC determined that WECC_URE1 failed to provide evidence that it had established Ratings for its Facilities that are consistent with its associated Facility Ratings Methodology. | FAC-009-1 | R1 | Medium | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because of its limited size and a single interconnection to the BPS. WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. | The date on which WECC_URE1 was subject to compliance with FAC-009-1 R1. | The date on which WECC_URE1 documented Facility Ratings consistent with its associated Facility Ratings Methodology. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan for FAC-009-1 R1. According to the Mitigation Plan, WECC_URE1 documented Facility Ratings as required by this Standard and submitted to WECC its Facility Rating Methodology spreadsheet as evidence of compliance. | 2010-09-08 | 2011-04-12 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001917 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence as requested by WECC on several occasions, WECC determined that WECC_URE1 failed to provide evidence that its operating personnel were familiar with the purpose and limitations of Protection System schemes applied in WECC_URE1's area. | PRC-001-1 | R1 | High | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE1 operates a small facility of less than 30 MW, and therefore, an unintended trip or a failure to trip could only impact WECC_URE1's equipment but would not have broader implications on the BPS. | The date on which WECC_URE1 was subject to compliance with PRC-001-1 R1. | The date on which WECC_URE1 implemented appropriate training. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan for PRC-001-1 R1 and R3. According to the Mitigation Plan, WECC_URE1 developed and implemented procedures and provided associated training to ensure that its operating personnel are familiar with the purposes and limitations of the Protection Systems applied in WECC_URE1's area. WECC_URE1 also implemented training to ensure that new Protection Systems or changes in the existing Protection Systems are coordinated with all appropriate entities. WECC_URE1 submitted a copy of the relevant procedures and training materials as evidence of compliance. | 2010-09-24 | 2010-11-16 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001919 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence as requested by WECC on several occasions, WECC determined that WECC_URE1 failed to provide evidence that it coordinated all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. | PRC-001-1 | R3 | High | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE1 confirmed that it had not experienced any protective system changes that would require Protection System changes by others, including the Transmission Operator and the Host Balancing Authority. In addition, the risk to the BPS was further mitigated by the limited size of the entity and the fact that it has only one interconnection point with the BPS. | The date on which WECC_URE1 was subject to compliance with PRC-001-1 R3. | The date on which WECC_URE1 implemented appropriate training. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan for PRC-001-1 R1 and R3. According to the Mitigation Plan, WECC_URE1 developed and implemented procedures and provided associated training to ensure that its operating personnel are familiar with the purposes and limitations of the Protection Systems applied in WECC_URE1's area. WECC_URE1 also implemented training to ensure that new Protection Systems or changes in the existing Protection Systems are coordinated with all appropriate entities. WECC_URE1 submitted a copy of the relevant procedures and training materials as evidence of compliance. | 2010-09-24 | 2010-11-16 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001922 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence as requested by WECC on several occasions, WECC determined that WECC_URE1 failed to provide evidence that it had a Protection System maintenance and testing program for Protection Systems that affect the reliability of the bulk power system (BPS), specifically addressing maintenance and testing intervals and their basis and a summary of maintenance and testing procedures. | PRC-005-1 | R1 | High | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the BPS because WECC_URE1 had acquired outside technical support to perform Protection System maintenance and testing but the documentation of this maintenance and testing did not completely address all of the elements that comprise its Protection System. The relay devices are documented but WECC determined that additional effort was needed to document maintenance and testing of DC circuitry, station batteries, associated communication equipment and voltage and current sensing devices. In addition, the risk to the BPS was further mitigated by the limited size of the entity and the fact that it has only one interconnection point with the BPS. | The date on which WECC_URE1 was subject to compliance with PRC-005-1 R1. | The date on which WECC_URE1 documented its Protection System maintenance and testing program. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan for PRC-005-1 R1 and R2.1. According to the Mitigation Plan, WECC_URE1 developed and implemented a documented Protection System maintenance and testing program (Program). The Program includes maintenance and testing intervals and their basis, and addresses relay protective devices, station batteries, voltage and current sensing devices, associated communication systems and DC control circuitry, as appropriate. The Program also includes a summary of maintenance and testing procedures for all BPS elements that comprise WECC_URE1's generator Protection System. As evidence of compliance, WECC_URE1 submitted a copy of the relevant program documents, a list of Protection System components, the schedule for maintenance and testing and documentation regarding testing and maintenance of its Protection System devices. | 2010-08-19 | 2011-03-22 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
WECC | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001923 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence as requested by WECC on several occasions, WECC determined that WECC_URE1 failed to provide evidence of its Protection System maintenance and testing program and the implementation of that program, including evidence that the Protection Systems were maintained and tested within the defined intervals, and the date each Protection System was last tested or maintained. | PRC-005-1 | R2.1 | High | Severe | WECC determined that the violation did not pose serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because although WECC_URE1 did not provide evidence that its Protection Systems were maintained and tested within defined intervals, WECC_URE1 subsequently provided evidence, as part of its Mitigation Plan completion, demonstrating that its Protection System devices had been tested and maintained. | The date on which WECC_URE1 was subject to compliance with PRC-005-1 R2. | The date on which WECC_URE1 documented testing and maintenance of its Protection System devices. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan for PRC-005-1 R1 and R2.1. According to the Mitigation Plan, WECC_URE1 developed and implemented a documented Protection System maintenance and testing program (Program). The Program includes maintenance and testing intervals and their basis, and addresses relay protective devices, station batteries, voltage and current sensing devices, associated communication systems and DC control circuitry, as appropriate. The Program also includes a summary of maintenance and testing procedures for all BPS elements that comprise WECC_URE1's generator Protection System. As evidence of compliance, WECC_URE1 submitted a copy of the relevant program documents, a list of Protection System components, the schedule for maintenance and testing and documentation regarding testing and maintenance of its Protection System devices. | 2010-08-19 | 2011-03-22 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002367 | Notice of Confirmed Violation | On January 26, 2010, WECC_URE2 submitted Self-Reports to WECC concerning violations of CIP-007-1 R3 and R6. On November 22, 2010, a WECC subject matter expert (SME) conducted an interview with WECC_URE2 personnel, and determined that WECC_URE2’s CIP-007 Self-Reports involved one server used for controlling physical access (doors) at three Physical Security Perimeters (PSPs). Then, the SME determined that CIP-007 does not cover such devices. Therefore, on December 30, 2010, WECC_URE2 replaced its CIP-007 Self-Reports with a single Self-Report addressing a violation of CIP-006-1 R1.8. In its new Self-Report, WECC_URE2 clarified that the server is used for physical access and monitoring its primary control center. A WECC SME reviewed WECC_URE2’s CIP-006-1 R1 Self-Report, and determined WECC_URE2 did not assess available security patches for the server and did not review the server’s system event logs. WECC determined that WECC_URE2’s failure to assess the available security patches or review the server’s system event logs did not afford the server the protective measures specified in CIP-007. | CIP-006-1 | R1 | Medium | Moderate | WECC determined that the violation of CIP-006-1 R1 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because WECC_URE2 stated that the access control and monitoring assets to its primary control center, including the server at issue, were in a facility that logged, detected, and alarmed for unauthorized physical and electronic access. | The date on which WECC_URE2 was subject to compliance with CIP-006-1 R1. | The date on which WECC_URE2 implemented an appropriate patch management system and enabled logging. | $20,400 (for WECC201002367, WECC201002323, and WECC201002324) | Self-Report | WECC_URE2 combined the update service of the cyber systems to the current server updated services database to better manage, audit, and report security patch management. WECC_URE2 enabled logging and is performing weekly log reviews as defined in its CIP-007 R6 cyber security event procedure. | 2010-03-01 | 2011-07-21 | Does Not Contest | WECC_URE2 had a documented internal compliance program (ICP) at the time of the violation that WECC considered as a mitigating factor in determining the penalty. WECC determined that the WECC_URE2 ICP has been reviewed and approved by an Authorized Entity Officer or equivalent, is fully documented, reviewed and approved by an Authorized Entity Officer or equivalent, and has an oversight position identified and staffed.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002323 | Notice of Confirmed Violation | WECC notified WECC_URE2 that WECC was initiating the semi-annual CIP Self-Certification process for the year ending 2009. On January 28, 2010, WECC_URE2 submitted a Self-Report to WECC concerning a violation of CIP-006-1 R6 due to WECC_URE2’s failure to implement a maintenance and testing program to ensure the functionality of WECC_URE2’s physical security systems. Although WECC_URE2 self-reported this violation, because WECC_URE2 self-reported during the Self-Certification submission period, WECC classified the discovery method for this violation as Self-Certification. On November 22, 2010, a WECC SME conducted an interview with WECC_URE2 personnel where WECC_URE2 clarified that it did not perform baseline testing prior to or on its mandatory compliance date. The SME determined that WECC_URE2 did not conduct testing on its system, which is comprised of a server, workstations, card readers, and door readers in order to provide locking and opening controls at access points. In addition, WECC_URE2’s system provides alarms and alerts to a centralized database, and is associated with three Physical Security Perimeters (PSPs), including WECC_URE2’s (1) data center, (2) primary control center, and (3) back-up control center. WECC determined, by not performing baseline testing, WECC_URE2 failed to implement a maintenance and testing program to ensure that WECC_URE2 physical security systems under CIP-006-1 R2-R4 function properly. | CIP-006-1 | R6 | Medium | Moderate | WECC determined that the violation of CIP-006-1 R6 posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE2 failed to implement a maintenance and testing program for the physical security systems for three PSPs, including the primary control center, backup control center and a data center. The physical security system was used for access control, monitoring and logging at these PSPs, and the failure to implement the maintenance and testing program could allow physical security systems to malfunction and potential unauthorized access to the PSPs. WECC determined, however, that the violation did not pose a serious or substantial risk to the BPS because the facilities had physical and electronic access logging, were continuously monitored including video monitoring of access points and weekly log reviews were conducted by WECC_URE2. In addition, WECC_URE2 has an incident response plan, and hardware alerts for a physical security device failure. | The date on which WECC_URE2 was subject to compliance with CIP-006-1 R6. | The date on which WECC_URE2 performed and documented baseline testing. | $20,400 (for WECC201002367, WECC201002323, and WECC201002324) | Self-Certification | WECC_URE2 performed a test in accordance with its CIP physical security maintenance test program in order to provide evidence to establish a documented baseline. | 2010-02-10 | 2010-12-15 | Does Not Contest | WECC_URE2 had a documented internal compliance program (ICP) at the time of the violation that WECC considered as a mitigating factor in determining the penalty. WECC determined that the WECC_URE2 ICP has been reviewed and approved by an Authorized Entity Officer or equivalent, is fully documented, reviewed and approved by an Authorized Entity Officer or equivalent, and has an oversight position identified and staffed.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002324 | Notice of Confirmed Violation | On October 21, 2010, WECC_URE2 discovered a possible violation of CIP-007-1 R5. Then, on November 10, 2010, WECC_URE2 submitted a Self-Report to WECC concerning a violation of CIP-007-1 R5 due to WECC_URE2’s failure to document procedural controls that enforce access authentication and accountability for all user activity for 31 devices, including switches, firewalls, and servers. On November 22, 2010, a WECC SME conducted an interview with WECC_URE2 personnel who clarified information from its Self-Report stating that where WECC_URE2 could not use automated software to enforce password complexity, WECC_URE2 has a procedure for doing annual password changes in manual fashion. WECC_URE2’s procedure calls for password cracking tools to validate if a password met the complexity requirements outlined in CIP-007 R5.3. The SME determined that after WECC_URE2 installed such password cracking/validation tools pursuant to WECC_URE2’s account management procedure, WECC_URE2’s test machines crashed. Therefore, WECC_URE2 created a process to maintain password complexity through accountability and witness documentation of password changes and complexity based on the requirements. Both WECC_URE2 and the SME determined that WECC_URE2 had to institute this accountability and witness process on 31 devices, including switches, firewalls, and servers located in WECC_URE2’s control center and data center, that were Critical Cyber Assets or Cyber Assets within the Electronic Security Perimeter. Nevertheless, WECC determined WECC_URE2 did not document the manual process associated with the 31 devices. | CIP-007-1 | R5 | Lower | Moderate | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because while WECC_URE2 did not update its documented account management procedures to reflect procedural controls, WECC_URE2 did in fact follow its manual process of annually changing passwords with manual authentication and witness controls. In addition, WECC_URE2 did enforce authentication and accountability of all user activity for systems access by establishing and implementing technical controls as required by the standard. | The date on which WECC_URE2 was subject to compliance with CIP-007-1 R5. | TBD | $20,400 (for WECC201002367, WECC201002323, and WECC201002324) | Self-Report | WECC_URE2 rewrote procedures to address manual processes that were occurring internally, and drafted additional procedures dealing with default, administrative and shared accounts to assist in sustaining compliance. WECC_URE2 completed a scheduled upgrade to its Energy Management System (EMS) to eliminate system dependencies on shared accounts. WECC_URE2 changed its accounts to the normal password expiration required by CIP-007 R5 password management procedure. WECC_URE2 documented previously undocumented user IDs as shared accounts and the domain automated password complexity and aging was enabled for these accounts as well. WECC_URE2 provided additional training of its CIP-007 R5 shared account management procedure in order to utilize automated task management solutions to schedule and escalate tasks. WECC_URE2 began adhering to and follow its existing procedures and tasks associated to changing shared accounts passwords when employees with access retire, leave employment or change job responsibilities. WECC_URE2 began adhering to and following its existing procedures and tasks associated to changing accounts passwords. WECC_URE2 generated unique user IDs for management personnel and follow complexity and aging requirements set forth within the procedure. WECC_URE2 began utilizing task management programs to alert the responsible personnel of specific tasks needing to be performed. WECC_URE2 began issuing, tracking and escalating tasks based on the relative due date of the task. WECC_URE2 began revising its CIP-007 R1 testing procedure to better align with test process and other standard requirement procedures to prevent or minimize overlooked areas. WECC_URE2 began revising its password procedures to better align the internal process to prevent or minimize adverse effects on system operations while maintaining compliance. WECC_URE2 began adhering to the procedures as well as automated task management, escalation and auditing in order to assist in sustaining future compliance. | 12/30/2011 (approved date) | TBD | Does Not Contest | WECC_URE2 had a documented internal compliance program (ICP) at the time of the violation that WECC considered as a mitigating factor in determining the penalty. WECC determined that the WECC_URE2 ICP has been reviewed and approved by an Authorized Entity Officer or equivalent, is fully documented, reviewed and approved by an Authorized Entity Officer or equivalent, and has an oversight position identified and staffed. WECC determined that WECC_URE2's prior violations of CIP-007-1 R1 and CIP-007-1 R6 should not serve as a basis for aggravating the penalty because the instant violation is sufficiently distinct due to the unique differences between Critical Cyber Assets (protected in accordance with CIP-007).